## Read Me
Adding ASHP Equipment to be Tested for Load Control Compatibility
Background Information | The purpose of this list is to develop a resource that helps Great River Energy's end use members and contractors identify ASHP models compatible with their current load management receivers, often associated with discounted electric rates for heating and/or cooling. This resource will also help contractors locate and use manufacturer- or distributor-supplied wiring instructions for connecting and programming compatible ASHP models when attached to load management systems.
Instructions | Please update the 'communicating outdoor units' and 'non-communicating outdoor units' sheets/tabs to list ducted, non-ducted, and/or mixed-ducted ASHP models you sell that meet the criteria for the GRE load management program. If additional third-party controls kits beyond Electro Industries' WF-DFHP1 are compatible with your products, please add those to the 'control for non-communicating' tab and note in the associated outdoor model number row in the non-communicating sheet.
Required Fields : All fields that are required to list the equipment are shaded in this salmon color.
Optional Fields: Fields that are not required, but would be useful, are shaded in this green color.
Compatibility Criteria | Each model must provide one of the following:
| A | Factory-equipped, integrated connection points for use with 2-wire utility load management systems.
| B | A manufacturer-supplied load management integration kit with manufacturer-issued instructions for connecting to a 2-wire relay-based (normally open or normally closed) utility load management receiver.
| C | A manufacturer- or distributor-endorsed load management integration kit with manufacturer-or distributor-approved instructions for connecting to a 2-wire relay-based utility load management receiver.
Each new model added to the list must be tested and confirmed in the field or at a distributor location by a GRE member utility representative.
Reference material
Additional Notes on Compatibility | Proper functionality is defined as providing the following load management signal responses:
| A | Cooling season events
A 50% reduction in kW demand during cooling events via one of the following methods:
1. A 50%+ throttle operation for the full duration of a control event.
2. A 15-minute on/15-minute off cycled approach*
| B | Heating season events
ASHP system must operate in a standby state (as close to full off as the system will allow) for the full duration of the control event (minimum of 80% demand reduction across duration of control event).
ASHP models can be enrolled in the load management rates and programs upon successfully completing a field test with staff from a local cooperative and supplying required documentation to MN ASHP Collaborative staff.
*Units using the cycled cooling approach that do not provide the full 15 minutes of on or off time will be deemed as not functioning properly.

## Communicating outdoor units
Manufacturer/Brand | Model family # (no tonnages or other information needed if control method is consistent w/in model family) | Refrigerant | Compressor Type (Variable speed, multi-stage) | Outdoor unit fan type (vertical / horizontal) | Ducted & mixed ducted | Non-ducted (ductless, minisplit) | Ducted (ducted, minisplit) | Includes control board contacts for load management relay? (url to wiring diagram) | Link for proprietary themostat controller integration with control board contacts (url to controller setup) | Additional components required? (if yes, please list) | Available for testing in distributor lab or warehouse? (this may allow faster product listing) | Link to wiring diagrams and installation documents | Notes
Example Entry - TVX | 555CBA | R-454B | Variable | Vertical | TRUE | FALSE | FALSE | Yes |  |  |  | Insert link to any document/video on installation here | Insert any applicable notes here

## Non-communicating outdoor units
Manufacturer/Brand | Model family # (no tonnages or other information needed if control method is consistent w/in family) | Refrigerant | Compressor Type (variable capacity systems greater than two-stage) | Outdoor unit fan type (vertical / horizontal) | Ducted & mixed ducted | Non-ducted (ductless, minisplit) | Ducted (ducted, minisplit) | Can be wired to interrupt partial or full line voltage power? (120V or 240V) | Compatible with third party controller? (if different than han Electro Industries' WF-DFHP, please specify) | Power outage restart delay time (minutes) | Available for testing in distributor lab or warehouse? (this may allow faster product listing) | Link to wiring diagrams and installation documents (optional - can use Stearns Electric Co-op example wiring diagram LM7) | Notes
Example Entry - TVX | 999ABC | R-454B | Variable Speed | Vertical | TRUE | FALSE | FALSE | Yes | Yes | 5 minutes | No | CAN USE EXAMPLE ABOVE | Insert any applicable notes here

## Controls for non-communicating (hidden)
Code | Manufacturer/Brand | Model Number | Wiring instructions/diagram link | Compatibility (Communicating / Non-communicating) | Notes
A | Electro Industries | WF-DFHP1 | HL101.pdf | Non-communicating | This Electro Industries product is fully compatible with heat pumps controlled by a 4-wire, 24V thermostat without the need for a Y2 wire.